## Slide 1
Extract characteristic module values from PAN File
Calculate photocurrent & diode reverse saturation current @ STC
Use calcparams_PVSyst function to generate the single diode model input parameters
Use singlediode function to calculate string DC power
Import matrix of 61853 test data
Use fit_efficiency_model to generate optimized values
Use model function to calculate efficiency
Convert normalized efficiency to DC power
Extract characteristic module values from PAN File
Use fit_cec_sam function to generate the input parameters
Use calcparams_cec/desoto function to generate the single diode model input parameters
Use singlediode function to calculate string DC power
CEC/Desoto
PVSyst
Matrix Models

## Slide 2
Model | Sandia Array Performance Model (SAPM) | PVWatts | Single Diode Models (CEC, Desoto, PVSyst) | Matrix Models (ADR, Heydenreich, MotherPV, PVGIS, MPM5, MPM6, Bilinear)
Input Parameters |  |  |  | 
Effective Irradiance | ✔ | ✔ | ✔ | ✔
Cell Temperature | ✔ | ✔ | ✔ | 
Module Temperature |  |  |  | ✔
SAPM Coefficients | ✔ |  |  | 
STC Power & Temperature Coefficient |  | ✔ |  | 
PAN File Coefficients |  |  | ✔ | 
61853 Matrix Data |  |  |  | ✔
Output Values |  |  |  | 
Isc | ✔ |  | ✔ | 
Imp | ✔ |  | ✔ | 
Vmp | ✔ |  | ✔ | 
Voc | ✔ |  | ✔ | 
Pmp | ✔ | ✔ | ✔ | 
Efficiency |  |  |  | ✔

## Slide 3
Manufacturer & Model | Cell Technology | # of Modules | Installation Date
LG 320N1K-A5 | N-PERT Si | 4 strings of 12 (48) | June 2018
Panasonic VBHN325SA16 | HIT Mono | 4 strings of 12 (48) | June 2018
Canadian Solar CS6K-270P | Poly-Si | 4 strings of 12 (48) | October 2017
Canadian Solar CS6K-275M | Mono-Si | 4 strings of 12 (48) | October 2017
Hanwha Q Cells Plus Q.Plus BFR-G4.1 280 | Poly-Si PERC | 4 strings of 12 (48) | October 2017
Hanwha Q Cells Peak Q.Peak BFR-G4.1 290 | Mono-Si PERC | 4 strings of 12 (48) | October 2017
Mission Solar MSE300SQ5T | Mono-Si PERC | 4 strings of 12 (48) | May 2019
Jinko Solar JKM260P-60 | Poly-Si | 4 strings of 12 (48) | April 2020*
Itek Energy IT-360-SE72 | Mono-Si PERC | 5 strings of 10 (50) | March 2020
*The Jinko system was initially installed in June 2016 but was later moved to the current configuration at the given date

## Slide 4
Filter Parameter | Lower Bound | Upper Bound
Solar Elevation | 15 deg | 90 deg
Effective Irradiance | 50 W/m2 | 1200 W/m2
Cell Temperature | -40 C | 85 C
Module Temperature | -40 C | 85 C
Ambient Temperature | -10 C | 40 C

## Slide 5
Notes: Modeled vs Measured power for SAPM model for LG System with temperature & irradiance as color

## Slide 6
Notes: SAPM mean absolute percent error on sunpath as color for LG System

## Slide 7
Notes: MAPE for individual LG System, can also be displayed as years on x and models as hue

## Slide 8
Can275 – All Years
Bounds used for filtering meteo data for PVPMC Intercomparison
Sol. Elev 15<x<90 – 60.62%
Eff Irr 50<x<1200 – 56.23%
Cell Temp -40<x<85 – 0.008%
Ratio of IvsG 0.004<x<0.008 – 56.48%
Total % Filtered for all years: 63.79%
Notes: Visualization of filters used on data for Can 275 system, can also be represented as the filter on top of the physical parameter itself (instead of on power like above)

## Slide 12
Notes: MBE for all systems & all models & all years, can also be displayed with models on x axis and systems as hue (next slide)

## Slide 14
PVWatts

## Slide 15
CEC

## Slide 16
Desoto

## Slide 17
PVSyst