## Slide 1
Import module dictionary using retrieve_sam or measured coefficients
Use pvsystem_sapm function to calculate string DC power
Extract characteristic module values from PAN File
Use pvwatts_dc function to calculate string DC power
Extract characteristic module values from specification sheet
Extract characteristic module values from PAN File
Use fit_cec_sam function to generate the input parameters
Extract characteristic module values from specification sheet
Use calcparams_cec/ desoto function to generate the single diode model input parameters
Use singlediode function to calculate string DC power
SAPM
PVWatts
CEC/Desoto

## Slide 2
Calculate photocurrent & diode reverse saturation current @ STC
Use fit_cec_sam function to generate the input parameters
Calculate photocurrent & diode reverse saturation current @ STC, diode ideality factor, and shunt resistance at 0 irradiance
Use calcparams_cec/ desoto function to generate the single diode model input parameters
Use singlediode function to calculate string DC power
Extract characteristic module values from PAN File
Extract characteristic module values from specification sheet
Import matrix of 61853 test data
Use fit_efficiency_model to generate optimized values
Use model function to calculate efficiency
Convert normalized efficiency to DC power
61853 Matrix Models
PVSyst

## Slide 3
Model | Sandia Array Performance Model (SAPM) | PVWatts | Single Diode Models (CEC, Desoto, PVSyst) | Matrix Models (ADR, Heydenreich, MotherPV, PVGIS, MPM5, MPM6, Bilinear)
Input Parameters |  |  |  | 
Effective Irradiance1 | ✔ | ✔ | ✔ | ✔
Measured Module Temp | ✔2 | ✔2 | ✔2 | ✔
SAPM Coefficients | ✔ |  |  | 
STC Power & Temperature Coefficient |  | ✔ |  | 
PAN File Coefficients |  |  | ✔ | 
61853 Matrix Data |  |  |  | ✔
Output Values |  |  |  | 
Isc | ✔ |  | ✔ | 
Imp | ✔ |  | ✔ | 
Vmp | ✔ |  | ✔ | 
Voc | ✔ |  | ✔ | 
Pmp | ✔ | ✔ | ✔ | 
Normalized Efficiency |  |  |  | ✔
1Calcualted using sapm_effective_irradiance which considers direct POA, diffuse POA, absolute airmass, and angle of incidence
2These modules use cell temperature, which is calculated from module temperature using pvlib.temperature.sapm_cell_from_module

## Slide 4
Manufacturer & Model | Cell Technology | # of Modules | Installation Date
LG 320N1K-A5 | N-PERT Si | 4 strings of 12 (48) | June 2018
Panasonic VBHN325SA16 | HIT Mono | 4 strings of 12 (48) | June 2018
Canadian Solar CS6K-270P | Poly-Si | 4 strings of 12 (48) | October 2017
Canadian Solar CS6K-275M | Mono-Si | 4 strings of 12 (48) | October 2017
Hanwha Q Cells Plus Q.Plus BFR-G4.1 280 | Poly-Si PERC | 4 strings of 12 (48) | October 2017
Hanwha Q Cells Peak Q.Peak BFR-G4.1 290 | Mono-Si PERC | 4 strings of 12 (48) | October 2017
Mission Solar MSE300SQ5T | Mono-Si PERC | 4 strings of 12 (48) | May 2019
Jinko Solar JKM260P-60 | Poly-Si | 4 strings of 12 (48) | April 2020*
Itek Energy IT-360-SE72 | Mono-Si PERC | 5 strings of 10 (50) | March 2020
*The Jinko system was initially installed in June 2016 but was later moved to the current configuration at the given date

## Slide 5
Filter Parameter | Lower Bound | Upper Bound
Solar Elevation | 15 deg | 90 deg
Effective Irradiance | 50 W/m2 | 1200 W/m2
Cell Temperature | -40 oC | 85 oC
Module Temperature | -40 oC | 85 oC
Ambient Temperature | -10 oC | 40 oC
Current vs Irradiance | 70% of slope of Imp/Geff | 130% of slope of Imp/Geff
Raw Data from Weather Station
Solar Elevation
Effective Irradiance
Cell & Module Temperature
Ambient Temperature
Imp/Geff
xx.xx% Remaining
xx.xx% Remaining
xx.xx% Remaining
xx.xx% Remaining
xx.xx% Remaining

## Slide 6
Notes: Modeled vs Measured power for SAPM model for LG System with temperature & irradiance as color

## Slide 7
Notes: SAPM mean absolute percent error on sunpath as color for LG System

## Slide 8
Notes: MAPE for individual LG System, can also be displayed as years on x and models as hue

## Slide 11
Notes: MBE for all systems & all models & all years, can also be displayed with models on x axis and systems as hue (next slide)

## Slide 15
Desoto